## StormCalcs
SIZE STORM DRAINAGE PIPING
RAINFALL | 2 | PIPE SLOPE | 1/8 inch per foot |  |  |  | TABLE 1106.2 STORM DRAIN PIPE SIZING | [5 empty] | TABLE 1106.3 VERTICAL LEADER SIZING
GUID | SYSTEM NAME | SLOPE "/12" | FLOW GPM | DIAMETER in | CLOSEST GREATER FLOW GPM | MIN. REQ.SIZE IN. | PIPE SIZE (inches) | CAPACITY (gpm) |  |  |  |  | SIZE OF LEADER (inches) | CAPACITY (gpm)
794373 | SD 1 | 1 | 33.6354 | 150 | 55 | 3 |  | VERTICAL DRAIN | SLOPE OF HORIZONTAL DRAIN |  |  |  | 2 | 30
794942 | SD 3 |  | 26.3586 | 150 | 55 | 3 |  |  | 1/16 inch per foot | 1/8 inch per foot | 1/4 inch per foot | 1/2 inch per foot | 2.5 | 54
794944 | SD 3 | 1 | 26.3586 | 150 | 55 | 3 | 2 | 34 | 15 | 22 | 31 | 44 | 3 | 92
795007 | SD 6 |  | 14.8085 | 100 | 22 | 2 | 3 | 87 | 39 | 55 | 79 | 111 | 4 | 192
795745 | SD 6 | 1 | 14.8085 | 100 | 22 | 2 | 4 | 180 | 81 | 115 | 163 | 231 | 5 | 360
841318 | SD 1 |  | 18.9252 | 150 | 22 | 2 | 5 | 311 | 117 | 165 | 234 | 331 | 6 | 563
841370 | SD 1 | 1 | 18.9252 | 150 | 22 | 2 | 6 | 538 | 243 | 344 | 487 | 689 | 8 | 1208
841561 | SD 1 | 0.98698 | 0 | 150 | 22 | 2 | 8 | 1117 | 505 | 714 | 1010 | 1429 | For SI: 1 inch = 25.4 mm, 1 gallon per minute = 3.785 L/m.
841684 | SD 1 |  | 18.9252 | 150 | 22 | 2 | 10 | 2050 | 927 | 1311 | 1855 | 2623
841727 | SD 6 | 1153966.2149 | 14.8085 | 100 | 22 | 2 | 12 | 3272 | 1480 | 2093 | 2960 | 4187
841910 | SD 1 | 120462.0185 | 14.7102 | 150 | 22 | 2 | 15 | 5543 | 2508 | 3546 | 5016 | 7093
842015 | SD 2 | 332642.1623 | 10.6593 | 100 | 22 | 2 | For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 gallon per minute = 3.785 L/m.
842781 | SD 2 | 0.95285 | 0 | 100 | 22 | 2
843199 | SD 2 |  | 10.6593 | 100 | 22 | 2
843543 | SD 1 | 1 | 33.6354 | 150 | 55 | 3
843546 | SD 1 |  | 33.6354 | 150 | 55 | 3
843728 | SD 1 | 0.99967 | 18.9252 | 150 | 22 | 2
843953 | SD 2 | 1387292.5719 | 10.3924 | 100 | 22 | 2
844002 | SD 2 | 1200292.0322 | 6.1569 | 100 | 22 | 2
844018 | SD 2 | 419463.5247 | 6.7576 | 100 | 22 | 2
844060 | SD 3 | 389043.6122 | 9.4276 | 100 | 22 | 2
844079 | SD 2 | 1 | 23.3069 | 150 | 55 | 3
844107 | SD 2 | 1 | 12.9144 | 150 | 22 | 2
844393 | SD 2 | 1.0024 | 23.3069 | 150 | 55 | 3
844608 | SD 2 | 1.003 | 0 | 150 | 22 | 2
844686 | SD 2 |  | 23.3069 | 150 | 55 | 3
844753 | SD 2 | 1 | 23.3069 | 150 | 55 | 3
844800 | SD 2 |  | 23.3069 | 150 | 55 | 3
844856 | SD 3 | 0.99965 | 16.931 | 150 | 22 | 2
844879 | SD 3 | 1 | 6.7576 | 100 | 22 | 2
844949 | SD 3 | 0.99934 | 26.3586 | 150 | 55 | 3
845042 | SD 3 | 1.0272 | 0 | 150 | 22 | 2
845345 | SD 3 | 0.99976 | 9.4276 | 100 | 22 | 2
846001 | SD 3 |  | 26.3586 | 150 | 55 | 3
846374 | SD 3 | 100 | 26.3586 | 150 | 55 | 3
846395 | SD 3 |  | 26.3586 | 150 | 55 | 3
847028 | SD 2 | 0.99887 | 10.6593 | 100 | 22 | 2
847059 | SD 1 | 0.99963 | 33.6354 | 150 | 55 | 3
847500 | SD 3 | 1 | 26.3586 | 150 | 55 | 3
847649 | SD 2 |  | 6 | 80 | 22 | 2
847701 | SD 2 |  | 6 | 80 | 22 | 2
848402 | SD 6 | 1 | 14.8085 | 100 | 22 | 2
848414 | SD 6 |  | 14.8085 | 100 | 22 | 2
848462 | SD 6 | 100 | 14.8085 | 100 | 22 | 2
849004 | SD 2 |  | 22.6593 | 100 | 55 | 3
849141 | SD 1 |  | 33.6354 | 150 | 55 | 3
849444 | SD 2 |  | 26.3069 | 150 | 55 | 3
850448 | SD 2 | 1 | 22.6593 | 100 | 55 | 3
850589 | SD 2 | 1.0022 | 26.3069 | 150 | 55 | 3
850836 | SD 2 | 1 | 6 | 80 | 22 | 2
850889 | SD 2 |  | 12 | 80 | 22 | 2
850946 | SD 2 | 100 | 6 | 80 | 22 | 2
850974 | SD 2 |  | 6 | 80 | 22 | 2
851044 | SD 2 | 100 | 6 | 80 | 22 | 2
851057 | SD 2 |  | 6 | 80 | 22 | 2
851168 | SD 2 | 0.99981 | 3 | 80 | 22 | 2
851233 | SD 2 |  | 3 | 80 | 22 | 2
852298 | SD 2 | 1.0011 | 12 | 80 | 22 | 2
852493 | SD 2 | 0.99921 | 12 | 80 | 22 | 2
852671 | SD 2 | 0.99921 | 12 | 80 | 22 | 2
852700 | SD 2 | 102.0186 | 12 | 80 | 22 | 2
852988 | SD 2 | 1.9999 | 48.9661 | 150 | 55 | 3
1330897 | SD 2 |  | 10.6593 | 100 | 22 | 2
1330904 | SD 2 | 1 | 0 | 80 | 22 | 2
1330938 | SD 2 | 1.0114 | 3 | 80 | 22 | 2
1331736 | SD 2 |  | 3 | 80 | 22 | 2
1331754 | SD 2 | 1 | 3 | 80 | 22 | 2
1331943 | SD 2 | 0.80012 | 3 | 80 | 22 | 2
1338504 | SD 2 | 0.99963 | 12 | 80 | 22 | 2
1338548 | SD 2 | 102.0046 | 12 | 80 | 22 | 2
1358681 | SD 6 | 9807891.9529 | 14.8085 | 100 | 22 | 2
1358694 | SD 6 | 0.99752 | 14.8085 | 100 | 22 | 2
1358896 | SD 6 | 1 | 0 | 100 | 22 | 2
1364839 | SD 1 | 0.85844 | 14.7102 | 150 | 22 | 2
1364977 | SD 1 | 0.99967 | 33.6354 | 150 | 55 | 3
1389554 | SD 2 | 0.81268 | 23.3069 | 150 | 55 | 3
1432000 | SD 1 | 0.99967 | 18.9252 | 150 | 22 | 2
1432121 | SD 1 | 102.0195 | 18.9252 | 150 | 22 | 2
1432133 | SD 1 | 0.99967 | 18.9252 | 150 | 22 | 2
1449525 | SD 2 | 1 | 10.6593 | 100 | 22 | 2
1449607 | SD 2 |  | 10.6593 | 100 | 22 | 2
1449626 | SD 2 | 0.99993 | 10.6593 | 100 | 22 | 2
1449700 | SD 2 | 0.99972 | 10.6593 | 100 | 22 | 2
1450701 | SD 1 | 0.68251 | 33.6354 | 150 | 55 | 3
1450745 | SD 2 | 0.62461 | 10.6593 | 100 | 22 | 2
1457794 | SD 1 | 0.73091 | 33.6354 | 150 | 55 | 3
1458425 | SD 2 | 0.79344 | 10.6593 | 100 | 22 | 2
1485972 | SD 3 | 232005.9916 | 6.7576 | 100 | 22 | 2
1486066 | SD 3 | 1.0029 | 6.7576 | 150 | 22 | 2
1486240 | SD 3 | 1.1987 | 6.7576 | 100 | 22 | 2
1486896 | SD 3 | 1.0081 | 9.4276 | 100 | 22 | 2
1488487 | SD 6 | 0.99979 | 0 | 100 | 22 | 2
1492434 | SD 2 | 249510.7868 | 3 | 80 | 22 | 2
1497873 | SD 6 | 0.53275 | 14.8085 | 100 | 22 | 2
1497895 | SD 6 | 1.0092 | 14.8085 | 100 | 22 | 2
1498229 | SD 6 | 0.99979 | 14.8085 | 100 | 22 | 2
1498235 | SD 6 | 1.0002 | 14.8085 | 100 | 22 | 2
1498398 | SD 6 | 1.0007 | 0 | 100 | 22 | 2
1517803 | SD 2 | 1 | 6.7576 | 100 | 22 | 2
1517839 | SD 2 | 1 | 6.7576 | 150 | 22 | 2
1517861 | SD 2 | 59.0761 | 6.7576 | 100 | 22 | 2
1517882 | SD 2 | 1 | 6.7576 | 100 | 22 | 2
1530535 | SD 2 | 100 | 23.3069 | 150 | 55 | 3
1530662 | SD 2 | 0.98663 | 23.3069 | 150 | 55 | 3
1530776 | SD 2 | 1.0022 | 0 | 150 | 22 | 2
1577107 | SD 3 | 110.4554 | 9.4276 | 100 | 22 | 2
1577120 | SD 3 | 0.99996 | 9.4276 | 100 | 22 | 2
1577873 | SD 3 | 59.0753 | 16.931 | 150 | 22 | 2
1577914 | SD 3 | 0.24204 | 16.931 | 150 | 22 | 2
1578096 | SD 3 | 0.99934 | 16.931 | 150 | 22 | 2
1578883 | SD 3 |  | 10.1734 | 100 | 22 | 2
1578935 | SD 3 | 57.735 | 10.1734 | 100 | 22 | 2
1578948 | SD 3 |  | 10.1734 | 100 | 22 | 2
1594088 | SD 6 | 0.98844 | 0 | 100 | 22 | 2
1671213 | SD 3 | 0.99934 | 26.3586 | 150 | 55 | 3
1671373 | SD 3 | 20.9322 | 26.3586 | 150 | 55 | 3
1671394 | SD 3 | 0.99934 | 26.3586 | 150 | 55 | 3
1705867 | SD 6 | 0.783 | 14.8085 | 100 | 22 | 2
1705883 | SD 6 | 1 | 14.8085 | 100 | 22 | 2
794946 | SD 3 |  | 26.3586 | 150 | 55 | 3
795761 | SD 6 |  | 14.8085 | 100 | 22 | 2
841386 | SD 1 |  | 18.9252 | 150 | 22 | 2
841549 | SD 1 |  | 18.9252 | 150 | 22 | 2
841590 | SD 1 |  | 33.6354 | 150 | 55 | 3
842539 | SD 2 |  | 10.6593 | 100 | 22 | 2
842737 | SD 2 |  | 10.6593 | 100 | 22 | 2
842810 | SD 2 |  | 48.9661 | 100 | 55 | 3
843568 | SD 1 |  | 33.6354 | 150 | 55 | 3
843741 | SD 1 |  | 33.6354 | 150 | 55 | 3
844091 | SD 2 |  | 6.7576 | 100 | 22 | 2
844102 | SD 2 |  | 12.9144 | 150 | 22 | 2
844106 | SD 2 |  | 23.3069 | 150 | 55 | 3
844596 | SD 2 |  | 23.3069 | 150 | 55 | 3
844633 | SD 2 |  | 48.9661 | 150 | 55 | 3
844692 | SD 2 |  | 23.3069 | 150 | 55 | 3
844764 | SD 2 |  | 23.3069 | 150 | 55 | 3
844808 | SD 2 |  | 23.3069 | 150 | 55 | 3
844878 | SD 3 |  | 16.931 | 150 | 22 | 2
846010 | SD 3 |  | 26.3586 | 150 | 55 | 3
846391 | SD 3 |  | 26.3586 | 150 | 55 | 3
846401 | SD 3 |  | 26.3586 | 150 | 55 | 3
847531 | SD 3 |  | 26.3586 | 150 | 55 | 3
847535 | SD 3 |  | 26.3586 | 150 | 55 | 3
848426 | SD 6 |  | 14.8085 | 100 | 22 | 2
848481 | SD 6 |  | 14.8085 | 100 | 22 | 2
848485 | SD 6 |  | 14.8085 | 100 | 22 | 2
849171 | SD 1 |  | 33.6354 | 150 | 55 | 3
850618 | SD 2 |  | 48.9661 | 150 | 55 | 3
850638 | SD 2 |  | 22.6593 | 100 | 55 | 3
850849 | SD 2 |  | 6 | 80 | 22 | 2
850897 | SD 2 |  | 6 | 80 | 22 | 2
850957 | SD 2 |  | 6 | 80 | 22 | 2
850982 | SD 2 |  | 6 | 80 | 22 | 2
851056 | SD 2 |  | 12 | 80 | 22 | 2
851061 | SD 2 |  | 6 | 80 | 22 | 2
852337 | SD 2 |  | 3 | 80 | 22 | 2
852580 | SD 2 |  | 12 | 80 | 22 | 2
852585 | SD 2 |  | 12 | 80 | 22 | 2
852743 | SD 2 |  | 12 | 80 | 22 | 2
852747 | SD 2 |  | 12 | 80 | 22 | 2
1037730 | SD 3 |  | 26.3586 | 150 | 55 | 3
1088073 | SD 2 |  | 26.3069 | 150 | 55 | 3
1330896 | SD 2 |  | 22.6593 | 100 | 55 | 3
1330906 | SD 2 |  | 48.9661 | 80 | 55 | 3
1331348 | SD 2 |  | 3 | 80 | 22 | 2
1331697 | SD 2 |  | 26.3069 | 150 | 55 | 3
1331760 | SD 2 |  | 3 | 80 | 22 | 2
1338572 | SD 2 |  | 12 | 80 | 22 | 2
1338576 | SD 2 |  | 12 | 80 | 22 | 2
1358874 | SD 6 |  | 14.8085 | 100 | 22 | 2
1358884 | SD 6 |  | 14.8085 | 100 | 22 | 2
1358949 | SD 6 |  | 14.8085 | 100 | 22 | 2
1364503 | SD 1 |  | 18.9252 | 150 | 22 | 2
1364972 | SD 1 |  | 14.7102 | 150 | 22 | 2
1364976 | SD 1 |  | 33.6354 | 150 | 55 | 3
1365326 | SD 1 |  | 33.6354 | 150 | 55 | 3
1365671 | SD 2 |  | 10.6593 | 100 | 22 | 2
1365689 | SD 1 |  | 33.6354 | 150 | 55 | 3
1432129 | SD 1 |  | 18.9252 | 150 | 22 | 2
1432168 | SD 1 |  | 18.9252 | 150 | 22 | 2
1432172 | SD 1 |  | 18.9252 | 150 | 22 | 2
1449624 | SD 2 |  | 10.6593 | 100 | 22 | 2
1449694 | SD 2 |  | 10.6593 | 100 | 22 | 2
1449699 | SD 2 |  | 10.6593 | 100 | 22 | 2
1458149 | SD 2 |  | 10.6593 | 100 | 22 | 2
1458195 | SD 1 |  | 33.6354 | 150 | 55 | 3
1458199 | SD 1 |  | 33.6354 | 150 | 55 | 3
1458488 | SD 2 |  | 10.6593 | 100 | 22 | 2
1458493 | SD 2 |  | 10.6593 | 100 | 22 | 2
1477135 | SD 2 |  | 3 | 80 | 22 | 2
1477139 | SD 2 |  | 3 | 80 | 22 | 2
1486321 | SD 3 |  | 6.7576 | 100 | 22 | 2
1486325 | SD 3 |  | 6.7576 | 100 | 22 | 2
1486976 | SD 3 |  | 9.4276 | 100 | 22 | 2
1486980 | SD 3 |  | 9.4276 | 100 | 22 | 2
1492444 | SD 2 |  | 3 | 80 | 22 | 2
1495265 | SD 6 |  | 14.8085 | 100 | 22 | 2
1497534 | SD 6 |  | 14.8085 | 100 | 22 | 2
1498228 | SD 6 |  | 14.8085 | 100 | 22 | 2
1498254 | SD 6 |  | 14.8085 | 100 | 22 | 2
1498356 | SD 6 |  | 14.8085 | 100 | 22 | 2
1498423 | SD 6 |  | 14.8085 | 100 | 22 | 2
1517878 | SD 2 |  | 6.7576 | 100 | 22 | 2
1517986 | SD 2 |  | 6.7576 | 100 | 22 | 2
1530551 | SD 2 |  | 23.3069 | 150 | 55 | 3
1530731 | SD 2 |  | 23.3069 | 150 | 55 | 3
1530761 | SD 2 |  | 23.3069 | 150 | 55 | 3
1531152 | SD 2 |  | 48.9661 | 150 | 55 | 3
1577115 | SD 3 |  | 9.4276 | 100 | 22 | 2
1577241 | SD 3 |  | 9.4276 | 100 | 22 | 2
1577245 | SD 3 |  | 26.3586 | 150 | 55 | 3
1577883 | SD 3 |  | 16.931 | 150 | 22 | 2
1578091 | SD 3 |  | 16.931 | 150 | 22 | 2
1578095 | SD 3 |  | 16.931 | 150 | 22 | 2
1578229 | SD 3 |  | 26.3586 | 150 | 55 | 3
1578943 | SD 3 |  | 10.1734 | 100 | 22 | 2
1578958 | SD 3 |  | 10.1734 | 100 | 22 | 2
1594076 | SD 6 |  | 14.8085 | 100 | 22 | 2
1594117 | SD 6 |  | 14.8085 | 100 | 22 | 2
1671389 | SD 3 |  | 26.3586 | 150 | 55 | 3
1671445 | SD 3 |  | 26.3586 | 150 | 55 | 3
1705882 | SD 6 |  | 14.8085 | 100 | 22 | 2
1705891 | SD 6 |  | 14.8085 | 100 | 22 | 2

## TABLE 1106.2 STORM DRAIN PIPE S
TABLE 1106.2 STORM DRAIN PIPE SIZING
PIPE SIZE (inches) | CAPACITY (gpm)
| VERTICAL DRAIN | SLOPE OF HORIZONTAL DRAIN
|  | 1/16 inch per foot | 1/8 inch per foot | 1/4 inch per foot | 1/2 inch per foot
2 | 34 | 15 | 22 | 31 | 44
3 | 87 | 39 | 55 | 79 | 111
4 | 180 | 81 | 115 | 163 | 231
5 | 311 | 117 | 165 | 234 | 331
6 | 538 | 243 | 344 | 487 | 689
8 | 1117 | 505 | 714 | 1010 | 1429
10 | 2050 | 927 | 1311 | 1855 | 2623
12 | 3272 | 1480 | 2093 | 2960 | 4187
15 | 5543 | 2508 | 3546 | 5016 | 7093
For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 gallon per minute = 3.785 L/m.

## TABLE 1106.3 VERTICAL LEADER SI
TABLE 1106.3 VERTICAL LEADER SIZING
SIZE OF LEADER (inches) | CAPACITY (gpm)
2 | 30
2 × 2 | 30
11/2 × 21/2 | 30
21/2 | 54
21/2 × 21/2 | 54
3 | 92
2 × 4 | 92
21/2 × 3 | 92
4 | 192
3 × 41/4 | 192
31/2 × 4 | 192
5 | 360
4 × 5 | 360
41/2 × 41/2 | 360
6 | 563
5 × 6 | 563
51/2 × 51/2 | 563
8 | 1208
6 × 8 | 1208
For SI: 1 inch = 25.4 mm, 1 gallon per minute = 3.785 L/m.